| Climate Control and Monitoring |  |  |  |  |
| --- | --- | --- | --- | --- |
| Originator: | Sender De La Roca |  | Effective Date: | September 26, 2024 |
| Manager Approval: | Sender De La Roca |  | Original Date: | September 26, 2024 |
|  |  |  | Revision Date: | September 26, 2024 |
| PURPOSE |  |  |  |  |
| The purpose of this procedure is to ensure the optimal operational conditions for servers, networking, and telecommunication equipment within the data center. This is achieved through precise climate control, advanced monitoring systems, and comprehensive fire protection measures. By following this procedure, data center staff can maintain the integrity and performance of all hardware components, promptly respond to environmental fluctuations, and safeguard the equipment and data housed within the facility |  |  |  |  |
| PROCEDURES |  |  |  |  |

1. Climate Control and Monitoring

1.1 CRAC Systems Operation

- Ensure that the Computer Room Air Conditioning (CRAC) systems are operational and providing precise cooling.

  - Each CRAC unit in the DATA Center can be accessed through their IP addresses.

  - IPs are 156.3.203.169 - .179

- Once you are logged on to each unit:

- Verify that the temperature is maintained within the range of 65 to 68 degrees Fahrenheit.

- Check that the relative humidity levels are within the recommended range of 45% to 55%.

1.2 Temperature and Humidity Monitoring

- Regularly monitor the temperature and humidity levels using the advanced monitoring systems installed in the data center.

- Log the temperature in the Computer Operations Shift Turnover to keep records of temperatures.

- Ensure that the monitoring systems are calibrated correctly and functioning as expected by resetting the wall monitors at least every three months. Power off/on each of the four control units to reset and calibrate.

- If they fail report to your supervisor.

1.3 Alert System

- The ECS team can confirm that the alert system is active and configured to notify administrators immediately if environmental conditions deviate from the established parameters.

- Test the email and text message notification system to ensure that data center staff receive alerts promptly by asking the ECS team to check the alert settings if there are any issues.

2. Infrastructure Management

2.1 Raised Floor Cleaning and Inspection.

- Twice a year, schedule authorized vendor to come to the Data Center to clean floor tiles.

- Inspect the raised floor design to ensure it enhances air circulation effectively.

- Verify that power cables and wires are routed efficiently beneath the raised floor, keeping them organized and out of the way.

2.2 Cooling Efficiency

- Regularly check the cooling efficiency of the data center to ensure that the raised floor design is contributing to optimal cooling.

- Address any obstructions or issues that may impede air circulation.

3. Fire Protection

3.1 Halon Gas System

- Perform annual and semi annual inspections and maintenance to the system by contacting authorized Vendor.

- Ensure that the halon gas fire suppression system is operational and ready to suppress fires without damaging sensitive electronic equipment.

3.2 Wet Pipe Sprinklers

- Verify that the wet pipe sprinkler system is functional and provides an additional layer of fire protection.

- Perform annual and semi annual inspections and maintenance to the system by contacting authorized Vendor.

3.3 Smoke Detectors

- Perform annual and semi annual inspections and maintenance to the system by contacting authorized Vendor.

- Test the smoke detectors regularly to ensure early detection of any fire-related incidents.