| Data Center Protocol: A/C Outage |  |  |  |  |
| --- | --- | --- | --- | --- |
| Originator: | Cesar Estrada |  | Revision Date: | September 23, 2016 |
| Manager Approval: | Rolando Mendoza |  | Effective Date: | October 1, 2014 |
|  |  |  | Original Date: | September 11, 2014 |
| Incident Handling |  |  |  |  |
| This procedure describes the series of steps and associated tasks to address the situation where in the Data Center has power but either A/C for the entire building is down or only the A/C system for the Data Center is non-operational. |  |  |  |  |
| Detailed Procedure |  |  |  |  |

# Indications

# All lights, equipment and hardware running as normal. Computer Room A/C (CRAC) units may not give out any sound at all when transitioning from chilled water to refrigerant (gas). All dual-mode CRAC units are running on backup mode (refrigerant) and not on chilled water. Panel on CRAC units will have displayed values on the snowflake “*” but have NONE on the “FC”.

# Action Items

# 2.1 Assessment.

# The first criterion to verify is whether the outage is planned or unplanned.

# Unless notified beforehand, call emergency contact numbers for Building Services and inquire about any events that may affect the AC system of the Data Center. Ascertain as possible to what extent the Data Center may have been affected. Where possible, ask details if available, as to expectations as to how long the outage will persist.

# Determine from the Building Services personnel if any of the chillers remain on line. If at least (1) chiller remains on functional, it has been determined that in an emergency situation, (1) of the newly installed chillers is capable of cooling the entire building.

# 2.2 Evaluation.

# 2.2.1 Unplanned Outage.

If HVAC outage will most likely persist beyond 15-30 minutes, the following areas need to be monitored for sharp  increases in temperature: network room (EC-163 75F), UPS room (EC-170 78F) and server room (EC-165 75F).

The Supervisor on site will call the Manager of Operations and appraise him of the situation. The Supervisor can undertake it himself or direct a staff member to  open up a trouble ticket and include as many details as available at that time.  At this point in time, progressive updates will start at 30 min intervals by email or messaging.

# 2.2.2 Planned Outage.

The Supervisor on site will notify the Manager of Operations and inform him that the planned outage has started and will need to notify The Manager of Operations in the event of any anomalies during the process.

# 2.3 Corrective Measures

# 2.3.1 UPS Room EC-170 (Planned or Unplanned Outage)

Since the DataAire A/C unit in EC-170 runs on chilled water only, it can quickly add to the heat generated by the transformers and cause the  temperature in the UPS room (EC-170) to rise by very quickly. To prevent this situation, turn OFF the DataAire unit in EC-170.

Proceed to turn on the split-A/C units installed in the transformer and UPS battery sections by pressing the on-off (“I/O”) switch once to activate the units. This step should be done prior to the room temperature reaching over 80F. By experience, we have seen that the split-A/C unit can readily lower the temperature within in < 30 mins. Otherwise, if the unit is turned on after the temperature has exceeded 90F, it can take over 1-2 hrs before the room temperature gets stabilized to below 78F.

Ensure that the door to EC-170 is closed to prevent any further heat load to the backup spilt-A/C system.

# 2.3.2 Network Control Center EC-163

To prevent the temperature rising in the network room , turn OFF the CRAC-11 unit in EC-169 which runs only on chilled water to prevent adding to the heat generation. Where possible, gracefully shutdown the MICR printers after the warrant printing has completed.

If the temperature continues to rise to close to 75F, turn ON the 120VAC-1.5TR spot cooler already situated inside EC-163\ and aimed at the network equipment generating the most heat. Remind Operations staff to empty the condensate bottles every (2) hours.

[Unplanned]

After these corrective measures have been completed, the frequency of updates by email or messaging can be made every hour.

[Planned]

Notify the Operations Manager by email or instant messaging when all temperature corrective measures are in place and activated.

# 2.3.3 EC-160 Open area (Planned or Unplanned Outage)

The CRAC units 7 & 9 run only on chilled water and as such, these can quickly add to the heat generated within the area. These CRAC units are to be turned OFF through the panel and reactivated only when the A/C service to the building is restored.

2.3.4 EC-165 Server Room

The CRAC units 1 -6 all run on dual mode (chilled water and refrigerant gas). OPS staff just need to ensure that the units are in fact on “backup mode”. This can be verified by either (1) feeling the temperature of the aire passing out through the floor vents and (2) glancing over the panel and verifying that the chilled water mode or “free cooling” indicated by the small “FC” icon is at 0%. This will return to 100% when the chillers are re-activated.

# 2.4 Monitoring The Incident

# 2.4.1 Unplanned Outage

Throughout the outage, ensure that all rooms are within temperature threshold limits. Otherwise, notify Building Services of any additional equipment needed for added air circulation. Keep close contact with Building Services for updates as to when services will be restored.

Provide updates by email or messaging to the Manager of Operations as these become available every hour until situations stabilizes and longer intervals become more appropriate i.e. every 2-3 hours.

Should the situation destabilize, immediately call the Operations Manager and perform tasks as needed again from the Assessment step until the situation regains its stability.

# 2.4.2 Planned Outage

Should the situation destabilize, immediately call the Operations Manager and perform tasks as needed again from the Assessment step until the situation regains its stability.

# Return to Service

Once it has been established by Building Services that the A/C system has been returned to service, Supervisor on site is advised to wait at least 1 hour after being notified by Building Services before giving instruction to perform the following tasks to return the Data Center to normal service:

- restart the DataAire chilled Water unit in EC-170

  - turn OFF the split A/C unit in EC-170

- restart the CRAC-11 unit in EC-168

- restart CRAC-7 and CRAC-9 in EC-160

# Conclusion

Before closing out the trouble ticket, make sure to include all pertinent details where possible. Notify the Operations Manager of the resolution of the situation by email or messaging.

Operational Notes:

The EC-170 Split-A/C unit is turned ON every Thursday (or once a week) to prevent the internal seals from drying up and not functioning when we need it in an emergency.